## Slide 1: Lintel beam(with arching)
Wettaka Emmanuel kitunga 9160560012
Lusungu Mwazikani Phiri 9160560013

## Slide 2: Lintel Beam
Lintels are horizontal structural member designed to carry loads above openings.
Although lintels may be constructed of grouted and reinforced concrete masonry units, precast or cast-in-place concrete, or structural steel, this PPT addresses reinforced concrete masonry lintels only.
Concrete masonry lintels have the advantages of easily maintaining the bond pattern, color, and surface texture of the surrounding masonry and being placed without need for special lifting equipment.
Notes: Introduction

## Slide 3: Design Loads
Distributed loads from the dead weight of the lintel, the dead weight of the masonry above, and any floor and roof loads, dead and live loads supported by the masonry; and concentrated loads from floor beams, roof joists, or other beams framing into the wall. Axial load carried by lintels is negligible. Most of these loads can be separated into the four types illustrated in Figure 1 The designer calculates the effects of each individual load and then combines them using superposition to determine the overall effect, typically by assuming the lintel is a simply supported beam.

## Slide 4: Types of Loads
Uniform Loads
Triangular Loads
Concentrated loads
Uniform Loads over a portion of the span

## Slide 5: Conditions For Arching Action
For some configurations, the masonry will distribute applied loads in such a manner that they do not act on the lintel. This is called arching action of masonry. Arching action can be assumed when the following conditions are met (see also Figure 2):
Masonry wall laid in running bond.
Sufficient wall height above the lintel to permit formation of a symmetrical triangle with base angles of 45 from the horizontal as shown in Figure 2.
At least 8 in. (203 mm) of wall height above the apex of the 45° triangle,
Minimum end bearing (4 in. (102 mm) typ.) is maintained,
Control joints are not located adjacent to the lintel.
Sufficient masonry on each side of the opening to resist lateral thrust from the arching action.

## Slide 7
When arching occurs, the wall weight supported by the lintel is taken as the wall weight within the triangular area below the apex (see Figure 2 and Table 2). This triangular load has a base equal to the effective span length of the lintel and a height of half the effective span. Any superimposed roof and floor live and dead loads outside this triangle are neglected, since they are assumed to be distributed to the masonry on either side of the lintel. Loads applied within the triangle need to be considered, however. Concentrated loads are assumed to be distributed as illustrated in Figure 3. The load is then resolved onto the lintel as a uniform load, with a magnitude determined by dividing the concentrated load by this length. In most cases, this results in a uniform load acting over a portion of the lintel span.

## Slide 9: Design Example
Design a lintel for a 12 in. (305 mm) normal weight concrete masonry wall laid in running bond with vertical reinforcement at 48 in. (1.2 m) o.c. The wall configuration is shown in Figure 5.

## Slide 10: Notations
b = width of lintel, in. (mm)
Dlintel = lintel dead load, lb./ft (kN/m)
Dwall = wall dead load, lb./ft (kN/m)
d = distance from extreme compression fiber to centroid of tension reinforcement, in. (mm)
f'm = specified compressive strength of masonry, psi (MPa)
h = half of the effective lintel span, L/2, ft (m)
L = effective lintel span, ft (m)
Mall = allowable moment, in.-lb. (Nm.)
Mlintel = maximum moment due to lintel dead load, in.-lb. (Nm)

## Slide 11: Calculation
Check for Arching Action. Determine the height of masonry required for arching action. Assuming the lintel has at least 4 in. (102 mm) bearing on each end, the effective span is:
L = 5.33 + 0.33 = 5.67 ft (1.7 m).
The height of masonry above the lintel necessary for arching to occur in the wall (from Figure 2) is h + 8 in. (203 mm) = L/2 + 8 in. = 3.5 ft (1.1 m). Based on an 8-in. (203-mm) high lintel, there is 18.0 - (3.33 + 4.0 + 0.67) = 10.0 ft (3.0 m) of masonry above the lintel. Therefore, arching is assumed and the superimposed uniform load is neglected.

## Slide 12
Design Loads. Because arching occurs, only the lintel and wall dead weights are considered. Lintel weight, from Table 1, for 12 in. (305 mm) normal weight concrete masonry units assuming an 8 in. (203 mm) height is Dlintel = 88 lb./ft (1.3 kN/m).
For wall weight, only the triangular portion with a height of 3.5 ft (1.1 m) is considered. From Table 2, wall dead load is:
Dwall = 63 lb/ft2 (3.5 ft )
= 221 lb./ft (3.2 kN/m) at the apex.
Maximum moment and shear are determined using simply supported beam relationships. The lintel dead weight is considered a uniform load, so the moment and shear are,

## Slide 13
Mlintel = Dlintel L2/8
= (88)(5.7)2/8
= 357 lb-ft (0.48 kN-m)
Vlintel = D lintel L/2
= (88)(5.7)/2 = 251 lb (1.1 kN)
For triangular wall load, moment and shear are,
Mwall = Dwall L2/12
= (221)(5.7)2/12
= 598 lb-ft (0.81 kN-m)
Vwall = Dwall L/4
= (221)(5.7)/4 = 315 lb (1.4 kN)

## Slide 14
Because the maximum moments for the two loading conditions occur in the same locations on the lintel (as well as the maximum shears), the moments and shears are superimposed and summed:
Mmax = 357 + 598
= 955 lb-ft
= 11,460 lb-in (1.3 kN-m)
Vmax = 251 + 315
= 566 lb (2.5 kN)

## Slide 15
Lintel Design. From Tables 3 and 4, a 12 x 8 lintel with one No. 4 (M#13) bar and 3 in. (76 mm) or less bottom cover has adequate strength (Mall = 22,356 lb.-in. (2.53 kN-m) and Vall = 2,152 lb. (9.57 kN)). In this example, shear was conservatively computed at the end of the lintel. However, Building Code Requirements for Masonry Structures (ref. 2) allows maximum shear to be calculated using a distance d/2 from the face of the support.